## Cover Page
2016 Risk Assessment Mitigation Phase
Investigation 16-10-015
Risk Spend Efficiency Workpapers to
Electric Infrastructure Integrity
(Chapter SDG&E-12-WP-RSE)
January 2017

## Analysis
SDGE - Electric Infrastructure Integrity
Baseline Residual Risk
Adjustment Factor | Score Category | Original | Original Baseline
1 | Frequency | 0.18257 | 5112.0772
| Safety Consequence | 4
| Reliability Consequence | 4
| Compliance Consequence | 5
| Financial Consequence | 4
[13 empty] | Baseline | 0.18257 | 4 | 4 | 5 | 4
[7 empty] | (000s) | [7 empty] | 40% | 20% | 20% | 20% | New Consequence Scores, weighted
| Controls | Enable |  | Project ID | Name | Description | Capital Cost (2017-2019) | OM Cost (2017-2019 average) | Annuity | New/Existing | Life of the Project | Rationale | Frequency % | New Frequency | Safety | Reliability | Compliance | Financial | Safety | Reliability | Compliance | Financial | New Score | New Score (for life of project) | Mitigation Weight | Calibrated, Weighted New Score | Cost | RSE | Rank
| Adjusted Baseline | 0 |  | Overhead | B2, B3, B21 | Services, poles, capacitors | -61623.5188 | -1416.3616 | -5167.7582 | Existing | 40 |  | -628.7062 | 1.3304 | 0 | 0 | 0 | 0 | 4000 | 2000 | 20000 | 2000 | 37252.0238 | -1285597.8624 | 63.5% | -816354.6426 | -118277.9836 | 6.902 | 1
| Weights on Each Mitigation | 1 |  | Underground | B3, B4, B11, B12 | Cable, live front transformers, DOE switches, services, CMP switches and manholes | -148933.05 | 0 | -12489.5496 | Existing | 40 |  | -104.2435 | 0.3729 | 0 | 0 | 0 | 0 | 4000 | 2000 | 20000 | 2000 | 10441.0879 | -213160.4278 | 32% | -68211.3369 | -148933.05 | 0.458 | 7
| Annuity instead of Capital Cost | 0 |  | Substation | B1, B5 | Aged infrastructure, CBM | -37490 | -253 | -3143.9175 | Existing | 40 |  | -3045.4294 | 5.7427 | 0 | 0 | 0 | 0 | 4000 | 2000 | 20000 | 2000 | 160796.7772 | -6227388 | 3% | -186821.64 | -47610 | 3.924 | 5
| Adjustment Factor | 1 |  | System modernization | B9 | Advanced SCADA | -8552.55 | 0 | -717.2182 | Existing | 40 |  | -1498.1794 | 2.9179 | 0 | 0 | 0 | 0 | 4000 | 2000 | 20000 | 2000 | 81700.1625 | -3063523.41 | 1.5% | -45952.8512 | -8552.55 | 5.373 | 3
|  |  |  | Overhead | P3, P6, P7, P8, P12, P13, P20 | True up QA/QC, 4kV modernization, distribution rebuild, long spans, small wire and connectors, coastal infrastructure, anchor rods, UAV switches | 142315.95 | 8147.75 | 11934.6386 | Existing | 40 |  | 2205.4227 | -3.844 | 0 | 0 | 0 | 0 | 4000 | 2000 | 20000 | 2000 | -107630.8326 | 4509716.394 | 63.5% | 2863669.9102 | 468225.95 | 6.116 | 2
|  |  |  | Underground | P8, P10 | Undergrounding, tee connectors | 98476.8 | 1472 | 8258.2804 | Existing | 40 |  | 90.6608 | 0.017051 | 0 | 0 | 0 | 0 | 4000 | 2000 | 20000 | 2000 | 477.4277 | 185385.98 | 32% | 59323.5136 | 157356.8 | 0.377 | 8
|  |  |  | Substation | P1, P5 | CBM expansion, 4kV modernization | 5686.75 | 47.15 | 476.8918 | Existing | 40 |  | 163.4417 | -0.11583 | 0 | 0 | 0 | 0 | 4000 | 2000 | 20000 | 2000 | -3243.1903 | 334210.7 | 3% | 10026.321 | 7572.75 | 1.324 | 6
|  |  |  | System modernization | P9, P12 | SCADA RTUs, bridged cutout switches | 21541.8 | 783.15 | 1806.4988 | Existing | 40 |  | 8283.7379 | -14.9414 | 0 | 0 | 0 | 0 | 4000 | 2000 | 20000 | 2000 | -418359.0008 | 16938843.12 | 1.5% | 254082.6468 | 52867.8 | 4.806 | 4

## Data
OVERHEAD |  |  | Notes (Jade Thiemsuwan) | Calculations
26.3% | % of system that is small wire prone to wires down |  | 850.8 - Projected Number of Energized Wire Downs Over a 20 Year Period (Whole System) 398.55 - Projected Number of Energzied Wire Downs Over a 20 Year Period (Non-FTZ Only) - Top 25% Energized Wire Down Reductions (Most Effective to Least Effective); Approx. 100 Projected Energized Wire Downs covers 78 of 618 Non-FTZ Circuits (Interpretation: 25% of risk exists in 12.6% of circuits) - $681.58 MM - Total Estimated Cost to Reconductor all #6 Wire in Non-FTZ - $309.92 Total Estimated Cost to Reconductor Top 25% (78 Circuits) - $24.86 Total Estimated Cost to Deploy Falling Conductor Detection (FCD) Advanced Protection System on Top 25% of Non-FTZ | System Wide #6 Wire: 8,068,395 Circuit Feet (22.372%) System Wide Wire Total: 34,490,699 Circuit Feet Non-FTZ #6 Wire: 3,837,504 Circuit Feet (26.3%) Non-FTZ All Wire: 14,591,022 Circuit Feet
9.137% | % slated to be replaced/remedied (2017 - 2019) |  | 9.14% - Estimated % Reconductored for 3-Year Cycle of 10-Year Program | 1168830 Circuit Feet (Top 25%) divided by Non-FTZ #6 Wire (3,837,504) = 30.4581% Over 10-Year Program 3.04581% Annual * 3-Year Cycle = 9.13743%
2 | Effectiveness
63.5% | Weight
prorate: 70% contribution of OH to the EII risk * 9% of bad asset replaced * 2 effectivness of targeting worst performers
UNDERGROUND
26.05% | % of UG system that is bad cable per cable model |  | 2015 Reliability Data: 26.05% (15.09 Cable_SAIDI of 57.92 System_SAIDI)
0.482% | % slated to be replaced (2017-2019) |  | 0.1256% | $21.9 MM Total Cost of Proactive Cable Replacement Program (Annual) 10,464 Miles (55,259,920 Circuit Feet) UG - 165,885 Total Number of Substructures & Padmount Equipment Estimated (Cable Ft. divided # Structures) = 333 feet per cable segment If cost is $5 MM/mile, $21.9 MM yields 4.38 miles or 23,126 feet (13.14 miles for 3-year cycle) 13.14 miles divided by 10,464 miles = ~.13%
10 | Effectiveness
32% | Weight
SUBSTATION
6 | Number of 4 kV substations remedied |  | 6 Substations Removed over 3-Year Cycle | 2 substations per year (4 distribution circuits) 3-Year Cycle: 6 Substations
29 | Count of 4 kV substations |  | 29 - 4 kV (4 kV Busses) System Wide, 155 Addl' Step-Down Stations
3% | Weight
SYSTEM MODERNIZATION
6962 | Count of bad switches |  | 6,962 Bridged Cut-Out, Field-Maintenance-Only (FMO) Switches, Projected Premature Failures (20% of inspections), or do not meet modern field Safety expectations
63.07% | % bad switches slated for replacement/remedied (2017-2019) |  | Targeting 4,391 of the above switches (63.07%)
1.5% | Weight

## Reference
| 1 - Risk Starting Value Lookup Question | AA1 Frequency | AA2 Safety Consequence | AA3 Reliability Consequence | AA4 Compliance Consequence | AA5 Financial Consequence | AA6 Baseline Risk Score | Calculated Baseline | Probability |  |  |  | Consequence
1 | SCG - Cyber Security | 0.18257 | 4 | 6 | 5 | 5 | 44548.1013 | 44548.1013 | 7 | 31.6228 | 7 |  | 7 | 10000000 | [17 empty] | OH: I have expanded on and corrected some of the wire down stats.
2, 8 | SDGE - Climate Change Adaptation | 0.057735 | 4 | 5 | 4 | 5 | 2655.8112 | 2655.8112 | 6 | 3.1623 | 6 |  | 6 | 1000000
3 | SCG - Employee, Contractor, Customer and Public Safety | 0.57735 | 6 | 4 | 3 | 4 | 233364.9788 | 233364.9788 | 5 | 0.57735 | 5 |  | 5 | 100000 |  |  | Before | [14 empty] | UG: It may not be practical to pursue an explicit argument for the 600-amp tee approach because our outage records do not detail these assets as the cause of failure (the category is generalized as connectors/splices/racks, etc.). Even with accurate quantification, given the large volume of these assets in the field and the relatively low volume of failures, the likelihood converges on a near-zero percentage. I used 2015 cable failure SAIDI data as an assumption of the cable asset failure rate; inferring that the associated equipment (connectors, padmount equipment, etc.) could be proportionally replaced alongside proactive cable upgrades in pursuit of mitigating UG risks altogether. I believe this approach would be in alignment with the current method of using the Live Front Transformer/Terminator budget to remove at-risk equipment in conjunction with planned cable replacement work.
4 | SCG - Records Management | 0.057735 | 5 | 5 | 5 | 4 | 4734.2722 | 4734.2722 | 4 | 0.18257 | 4 |  | 4 | 10000 |  |  | Safety | [7 empty] | Compliance
5 | SCG - Workforce Planning | 0.57735 | 4 | 4 | 4 | 4 | 5773.5027 | 5773.5027 | 3 | 0.057735 | 3 |  | 3 | 1000 | Frequency | 7 | [7 empty] | 7 | [7 empty] | SUB: the “questionable asset” is assumed to be 4 kV substations (those containing 4 kV busses). There are 29 of these according to my records. A handful of these represent the package/unit substations (single point of failure could cause catastrophic damage), most of which could possibly be removed in one or two GRC cycles. There are several more 4 kV assets in the system, however they are considered to be in a lower risk category because they have likely experienced at least one generation of modernization (converted to padmount, undergrounded, etc.). Note that 4 kV distribution is an entirely different category of risk.
6 | SCG - Workplace Violence | 0.057735 | 6 | 1 | 2 | 3 | 23106.8279 | 23106.8279 | 2 | 0.018257 | 2 |  | 2 | 100 |  | 6 | [7 empty] | 6
7 | SDGE - Cyber Security | 0.18257 | 4 | 6 | 5 | 5 | 44548.1013 | 44548.1013 | 1 | 0.0054772 | 1 |  | 1 | 10 |  | 5 | [7 empty] | 5 | [7 empty] | Modernization: I provided data queried from GIS for a certain population of switches that we wish to address for risk mitigation. I only counted the switches that we would propose to replace, however the overall benefit of the proposed program also includes O&M activities that are not replacements. We should be careful when describing this program, as the switches are not necessarily “bad.” The program aims to improve worker and public safety, which is likely to occur if a switch is safer to operate or less prone to hot spots (e.g. OH disconnect switches). There are possible operational/procedural “workarounds” for some failed switches (e.g. DOE switches often remain in operation), however this program aims to achieve balance between reliability and safety. Furthermore, the Modernization category should be understood as a safety improvement program, not merely a reliability improvement.
9 | SDGE - Employee, Contractor & Public Safety | 0.18257 | 6 | 4 | 4 | 3 | 73796.4859 | 73796.4859 | [7 empty] | 4 | [7 empty] | 4
10 | SDGE - Records Management | 0.057735 | 5 | 5 | 5 | 4 | 4734.2722 | 4734.2722 | Weights | [6 empty] | 3 |  |  |  |  | 1 |  |  | 3 |  |  | 1 |  |  |  |  | I did not make any modifications to the effectiveness or weighting factors. In general, I am agreeable to the defaulted weights, seeing that the overhead category is an overwhelming majority. At your discretion, I offer these considerations for the other categories:
11 | SDGE - Workforce Planning | 0.057735 | 4 | 3 | 3 | 2 | 255.1888 | 255.1888 | 40% | Safety | [5 empty] | 2 | [7 empty] | 2 | [7 empty] | - UG: with 61% of SDG&E’s infrastructure being underground, there are many padmounted structures that are susceptible to public contact (e.g. car contact)
12 | SDGE - Workplace Violence | 0.057735 | 6 | 1 | 2 | 3 | 23106.8279 | 23106.8279 | 20% | Reliability | [5 empty] | 1 | [7 empty] | 1 | [7 empty] | - SUB: as these facilities are not public-accessible under normal circumstances, the only practical risk is employee contact incidents, which have not been notably common and are often mitigated by following proper procedures
13 | SDGE - Aviation Incident | 0.057735 | 6 | 2 | 2 | 3 | 23107.8672 | 23107.8672 | 20% | Compliance | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | - Modernization: obsolete or non-“intelligent” equipment may cause or otherwise delay the detection of energized wire down incidents. Similar to a wire down, exposed cable as a result of vehicle contact with single-phase padmounted equipment (i.e. residential transformer) could cause energized equipment exposure to the public.
14 | SDGE - Distributed Energy Resources (DERs) Safety and Operational Concerns | 0.18257 | 6 | 3 | 3 | 3 | 73139.2188 | 73139.2188 | 20% | Financial | [6 empty] | Impact | [7 empty] | Impact | [6 empty] | - Perhaps the weightings could be OH > Modernization > UG > SUB?
15 | SDGE - Electric Infrastructure Integrity | 0.18257 | 4 | 4 | 5 | 4 | 5112.0772 | 5112.0772 |  |  |  | 31.6228 | [19 empty] | In any case, please make the necessary modifications based on your interpretations of the provided figures.
16 | SDGE - Fail to Black Start | 0.018257 | 6 | 7 | 5 | 5 | 44548.1013 | 44548.1013 |  | 173.2051 |  | 31.653 |  |  |  |  | Reliability | [7 empty] | Finance
17 | SDGE - Major Disturbance to Electrical Service (e.g. Blackout) | 0.018257 | 6 | 7 | 5 | 5 | 44548.1013 | 44548.1013 |  | 17.3205 |  | 0.15811 |  |  | Frequency | 7 | [7 empty] | 7
18 | SDGE - Public Safety Events - Electric | 0.057735 | 5 | 3 | 3 | 3 | 2344.0421 | 2344.0421 |  | 3.1623 | [5 empty] | 6 | [7 empty] | 6
19 | SDGE - Unmanned Aircraft System (UAS) Incident | 0.018257 | 6 | 4 | 3 | 4 | 7379.6486 | 7379.6486 | [7 empty] | 5 | [7 empty] | 5
20 | SDGE - Wildfires caused by SDG&E Equipment (including 3rd Party Pole Attachments) | 0.57735 | 7 | 6 | 5 | 6 | 2551888.1898 | 2551888.1898 | [7 empty] | 4 | [7 empty] | 4
21 | SCG - Catastrophic Damage involving Gas Infrastructure (Dig-Ins) | 0.57735 | 6 | 4 | 3 | 4 | 233364.9788 | 233364.9788 | [7 empty] | 3 |  |  | 1 |  |  |  |  | 3 |  |  | 1
22 | SCG - Catastrophic Damage Involving Gas Transmission Pipeline Failure | 0.057735 | 6 | 5 | 5 | 6 | 36950.4172 | 36950.4172 | [7 empty] | 2 | [7 empty] | 2
23 | SCG - Catastrophic Damage involving Medium and Non-DOT Pipeline Failure | 0.057735 | 5 | 3 | 3 | 3 | 2344.0421 | 2344.0421 | [7 empty] | 1 | [7 empty] | 1
24 | SCG - Catastrophic Event related to Storage Well Integrity | 0.018257 | 5 | 5 | 5 | 5 | 1825.7419 | 1825.7419 | [8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
25 | SCG - Physical Security of Critical Infrastructure | 0.057735 | 5 | 6 | 4 | 4 | 14087.3466 | 14087.3466 | [8 empty] | Impact | [7 empty] | Impact
26 | SDGE - Catastrophic Damage involving Gas Infrastructure (Dig-Ins) | 0.57735 | 6 | 4 | 3 | 4 | 233364.9788 | 233364.9788
27 | SDGE - Catastrophic Damage Involving Gas Transmission Pipeline Failure | 0.018257 | 6 | 4 | 5 | 6 | 11356.1144 | 11356.1144 | [8 empty] | After
28 | SDGE - Catastrophic Damage Involving Medium and non-DOT Pipeline Failure | 0.057735 | 5 | 3 | 3 | 3 | 2344.0421 | 2344.0421 | [8 empty] | Safety | [7 empty] | Compliance
| SDGE - Violation of Environmental Policies/Procedures | 0.057735 | 4 | 1 | 5 | 4 | 1501.2262 | 1501.2262 | [6 empty] | Frequency | 7 | [7 empty] | 7
[16 empty] | 6 | [7 empty] | 6
[16 empty] | 5 | [7 empty] | 5
[16 empty] | 4 | [7 empty] | 4
[16 empty] | 3 |  |  |  |  | 1 |  |  | 3 |  |  | 1
[16 empty] | 2 | [7 empty] | 2
[16 empty] | 1 | [7 empty] | 1
[17 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
[17 empty] | Impact | [7 empty] | Impact
[17 empty] | Reliability | [7 empty] | Finance
[15 empty] | Frequency | 7 | [7 empty] | 7
[16 empty] | 6 | [7 empty] | 6
[16 empty] | 5 | [7 empty] | 5
[16 empty] | 4 | [7 empty] | 4
[16 empty] | 3 |  |  | 1 |  |  |  |  | 3 |  |  | 1
[16 empty] | 2 | [7 empty] | 2
[16 empty] | 1 | [7 empty] | 1
[17 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
[17 empty] | Impact | [7 empty] | Impact