## Specialized Audit Results
| Information in columns B, F, G, H, J, K, M & N are CONFIDENTIAL protected information being submitted to the CPUC pursuant to PUC §583 and all applicable protections. The detailed justification is provided in Attachment A of the accompanying Declaration. | [7 empty] | Expected Savings
Savings from Specialty Port Audits
Expected Savings
X | Customer | Audit Finding | Measure Type | Reason | Measure | kWh Savings from Audit | Therm Savings from Audit | Implementation Probability | kWh saved | Therms Saved | Measure Effective Useful Life | Lifetime kWh Saved | GHG metric tons
x | Continental Maritime | EEM-1 | Standard | Industrial Process; To Code Measure | Install retrofit variable speed drives on the rotary screw air compressors | 306305 | 0 | 50% | 153152.5 | 0 | 5 | 765762.5 | 38.6448
| Continental Maritime | EEM-2 | Standard | EEBI | Increase air compressor storage w/ new 1,000 gal capacity tank | 44980 | 0 | 50% | 22490 | 0 |  |  | 5.6749
| Continental Maritime | EEM-3 | Standard | ZELDA | Utilize zero loss condensate drains on compressed air system | 21480 | 0 | 50% | 10740 | 0 |  |  | 2.71
| Continental Maritime | EEM-4 | Standard | EEBI | optimize compressed air sequencing PID controls | 84110 | 0 | 50% | 42055 | 0 |  |  | 10.6117
x | Continental Maritime | EEM-5 | Specialized | Temporary/Portable; Ownership | specify high efficiency temporary air compressors | 215000 | 0 | 20% | 43000 | 0 | 15 | 645000 | 10.8502
x | Continental Maritime | EEM-6 | Specialized | Temporary/Portable; Ownership | install VFDs at stand-alone ventilation fans | 186440 | 0 | 50% | 93220 | 0 | 5 | 466100 | 23.5221
| Continental Maritime | EEM-7 | Standard | EEBI | install VFDs at Shop exhaust fan & provide 8 hr. shutoff control | 4610 | 0 | 20% | 922 | 0 |  |  | 0.23265
| Continental Maritime | EEM-8 | Standard | EEBI | Upgrade Admin Bldg. w/ HVAC Wi-Fi thermostats w/occ sensors | 54695 | 0 | 20% | 10939 | 0 |  |  | 2.7602
| Continental Maritime | EEM-9 | Standard | EEBR | Upgrade lighting in Admin bldg. from T-8 to led (Tube Only Option) | 101114 | 0 | 50% | 50557 | 0 |  |  | 12.757
| Continental Maritime | EEM-10 | Standard | EEBR | Upgrade lighting in Admin Bldg. from t-8 to LED (Fixture Option) | 87887 | 0 | 20% | 17577.4 | 0 |  |  | 4.4353
| Continental Maritime | EEM-11 | Standard | EEBR | Replace high bay warehouse & shop T-8 fluorescent fixtures with LEDs | 28655 | 0 | 20% | 5731 | 0 |  |  | 1.4461
x | Continental Maritime | EEM-12 | Standard | EEBI for Control System Only | Utilize natural light (solar tubes in roof) for daylight harvesting at warehouse | 9841 | 0 | 20% | 1968.2 | 0 | 15 | 29523 | 0.49663
x | Continental Maritime | EEM-13 | Specialized | Temporary/Portable; Ownership | retrofit stringer lighting with LEDs | 59870 | 0 | 50% | 29935 | 0 | 15 | 449025 | 7.5535
x | Continental Maritime | EEM-14 | Specialized | Temporary/Portable; Ownership | Replace sandblast nozzles with worn aperture opening greater than 20% | 29545 | 0 | 50% | 14772.5 | 0 | 5 | 73862.5
x | Continental Maritime | EEM-15 | Specialized | Temporary/Portable; Ownership | Upgrade sandblast nozzles to suction/blast/venturi amplification blast type | 37310 | 0 | 50% | 18655 | 0 | 5 | 93275
x | BAE Systems | EEM-1 | Specialized | Temporary/Portable; Ownership | Install VFDs at the stand alone ventilation fans and provide controls | 315360 | 0 | 50% | 157680 | 0 | 5 | 788400 | 39.7873
x | BAE Systems | EEM-2 | Specialized | Temporary/Portable; Ownership | Install retrofit VFDs on large Pier portable air compressors | 555795 | 0 | 50% | 277897.5 | 0 | 5 | 1389487.5 | 70.1217
| BAE Systems | EEM-3 | Standard | ZELDA | Utilize zero loss condensate drains on compressed air system | 39849 | 0 | 50% | 19924.5 | 0 |  |  | 5.0275
x | BAE Systems | EEM-4 | Specialized | Temporary/Portable; Ownership | specify high efficiency temporary air compressors | 179620 | 0 | 20% | 35924 | 0 | 15 | 538860 | 9.0647
x | BAE Systems | EEM-5 | Specialized | Temporary/Portable; Ownership | Specify induction type portable welding machines to replace existing types | 272120 | 0 | 50% | 136060 | 0 | 15 | 2040900 | 34.3319
x | BAE Systems | EEM-6 | Specialized | Temporary/Portable; Ownership | Specify/purchase high efficiency packaged AC unit with Catalyst controls | 122399 | 0 | 50% | 61199.5 | 0 | 15 | 917992.5 | 15.4424
x | BAE Systems | EEM-7 | Specialized | Temporary/Portable; Ownership | retrofit stringer lights with LEDs | 93670 | 0 | 50% | 46835 | 0 | 15 | 702525 | 11.8178
x | BAE Systems | EEM-8 | Specialized | Temporary/Portable; Ownership | High efficiency electrical transformers | 89640 | 0 | 20% | 17928 | 0 | 20 | 358560 | 4.5238
x | BAE Systems | EEM-9 | Specialized | Temporary/Portable; Ownership | Replace sandblast nozzles with worn aperture opening greater than 20% | 146400 | 0 | 50% | 73200 | 0 | 5 | 366000 | 18.4705
x | BAE Systems | EEM-10 | Specialized | Temporary/Portable; Ownership | Upgrade sandblast nozzles to suction/blast/venturi amplification blast type | 191340 | 0 | 50% | 95670 | 0 | 5 | 478350 | 24.1403
| convention center | EEM-1 | Standard | EEBR | Exhibit Hall LED Lighting Fixture Upgrade | 680146 |  | 50% | 340073 | 0 |  |  | 85.8103
| convention center | EEM-2 | Standard | EEBR | Interior Lighting Upgrade | 1418704 |  | 80% | 1134963.2 | 0 |  |  | 286.3844
| convention center | EEM-3 | Standard | EEBR | Sails Pavilion High Eff Boiler Replacement | 0 | 2270 | 20% | 0 | 454 |  |  | 2.4156
| convention center | EEM-4 | Standard | EEBI | Sails Pavilion High Eff Chiller Replacement | 65250 |  | 20% | 13050 | 0 |  |  | 3.2929
| convention center | EEM-5 | Standard | EEBI | Sails Pavilion CHW Tie-in | 194913 |  | 50% | 97456.5 | 0 |  |  | 24.5911
| convention center | EEM-6 | Standard | EEBI | Convert Sails Pavilion CHW to variable flow | 23250 |  | 50% | 11625 | 0 |  |  | 2.9333
| convention center | EEM-7 | Standard | EEBI | Sails Pavilion Natural Ventilation | 182728 |  | 20% | 36545.6 | 0 |  |  | 9.2215
| convention center | EEM-8 | Standard | EEBI | Central Plant Optimization Software | 554140 |  | 80% | 443312 | 0 |  |  | 111.8606
| convention center | EEM-9 | Standard | EEBI | Decouple Secondary CHW Loop | 188484 |  | 20% | 37696.8 | 0 |  |  | 9.512
| convention center | EEM-10 | Standard | EEBI | Pre-Cool CW Loop with Dewatering Pumps | 146000 |  | 20% | 29200 | 0 |  |  | 7.368
| convention center | EEM-11 | Standard | RCx | Implement a HHW Reset Strategy | 19772 | 11042 | 20% | 3954.4 | 2208.4 |  |  | 12.7479
| convention center | EEM-12 | Standard | EEBR | Exhibit Hall AHU’s VAV Conversion | 979000 | -435 | 80% | 783200 | -348 |  |  | 195.7726
| convention center | EEM-13 | Standard | EEBI | Meeting Room and Lobby AHU's VFD Upgrade | 627000 | -279 | 80% | 501600 | -223.2 |  |  | 125.3808
x | convention center | EEM-14 | Standard | Energy Dashboard; Operational Improvement | Continuous Commissioning Software | 80000 | 3000 | 80% | 64000 | 2400 | 3 | 192000 | 28.9186
| convention center | EEM-15 | Standard | EEBR | Low-E Window Film Installation | 61080 | -380 | 20% | 12216 | -76 |  |  | 2.6781
| convention center | EEM-16 | Standard | EEBI | Escalator Variable Torque Controllers | 228632 |  | 80% | 182905.6 | 0 |  |  | 46.1524
x | Harborside | EEM-1 | Standard | Industrial Process; Operational Improvement | Raise Freezer temperature to 0F | 51358 |  | 20% | 10271.6 | 0 | 3 | 30814.8 | 2.5918
x | Harborside | EEM-2 | Standard | Industrial Process; Operational Improvement | Increase high stage suction pressure setpoint | 71343 |  | 20% | 14268.6 | 0 | 3 | 42805.8 | 3.6004
x | Harborside | EEM-3 | Standard | Industrial Process; Operational Improvement | Lower condensing pressure setpoint | 103816 |  | 20% | 20763.2 | 0 | 3 | 62289.6 | 5.2392
| Harborside | EEM-4 | Standard | EEBI | Close openings in ceiling of rooms T & V | 9677 |  | 80% | 7741.6 | 0 |  |  | 1.9534
| Harborside | EEM-5 | Standard | EEBI | Add VFD to freezer compressor | 121634 |  | 50% | 60817 | 0 |  |  | 15.3459
| Harborside | EEM-6 | Standard | EEBI | Add VFD to cooler compressor | 172512 |  | 50% | 86256 | 0 |  |  | 21.7649
| Harborside | EEM-7 | Standard | EEBR | Upgrade warehouse, Cooler , and Freezer Highbay lighting Fixtures to LED | 290324 |  | 50% | 145162 | 0 |  |  | 36.6286
| Harborside | EEM-8 | Standard | EEBR | Upgrade office lighting Fixtures to LED | 4837 |  | 20% | 967.4 | 0 |  |  | 0.2441
| Harborside | EEM-9 | Standard | EEBI | installl lighting Occ sensors in warehouse , cooler and freezer space | 22491 |  | 20% | 4498.2 | 0 |  |  | 1.135
| Harborside | EEM-10 | Standard | EEBI | Add VFDs to condenser fans | 26000 |  | 20% | 5200 | 0 |  |  | 1.3121
| Harborside | EEM-11 | Standard | EEBI | Add VFDs to evaportor fans | 150000 |  | 50% | 75000 | 0 |  |  | 18.9247
| SD Cold | EEM-1 | Standard | EEBI | Upgrade Control System | 141201 | 0 | 20% | 28240.2 | 0 |  |  | 7.1258
x | SD Cold | EEM-2 | Standard | Industrial Process; Operational Improvement | Adjust CPR Pressure regulator setting | 6519 | 0 | 20% | 1303.8 | 0 | 5 | 6519 | 0.32899
| SD Cold | EEM-3 | Standard | EEBI | Optimize Freezer Defrost Settings | 21745 | 0 | 20% | 4349 | 0 |  |  | 1.0974
| SD Cold | EEM-4 | Standard | EEBI | Add VFDs to evaportor fans | 60000 | 0 | 50% | 30000 | 0 |  |  | 7.5699
| SD Cold | EEM-5 | Standard | EEBI | Add VFDs to condenser fans | 23282 | 0 | 50% | 11641 | 0 |  |  | 2.9374
| SD Cold | EEM-6 | Standard | EEBR | Upgrade warehouse, Cooler , and Freezer Highbay lighting Fixtures to LED | 225670 | 0 | 50% | 112835 | 0 |  |  | 28.4716
| SD Cold | EEM-7 | Standard | EEBR | Upgrade office lighting Fixtures to LED | 5212 | 0 | 20% | 1042.4 | 0 |  |  | 0.26303
| SD Cold | EEM-8 | Standard | EEBI | install lighting Occ sensors in warehouse , cooler and freezer space | 22108 | 0 | 20% | 4421.6 | 0 |  |  | 1.1157
| Solar Turbines | EEM-1 | Standard | EEBI | High Pressure Compressed Air Controls | 1166833 | 0 | 50% | 583416.5 | 0 |  |  | 193.7477
| Solar Turbines | EEM-2 | Standard | EEBI | Gas Compressor Part Load Controls | 399582 | 0 | 50% | 199791 | 0 |  |  | 159.4424
x | NASSCO1 |  | Specialized | Temporary/Portable; Ownership | Temporary Lighting Conversion to LED |  |  |  | 240000 |  | 15 | 3600000
x | US Navy2 |  | Specialized | Temporary/Portable; Ownership | Living Barge Energy Efficiency Upgrades |  |  |  | 500000 |  | 15 | 7500000
[5 empty] | Total From Specialty Audits |  |  | Total From Specialty Audits | 7277817.3 | 4415.2 |  | 21538052.2 | 1820.3032
[5 empty] | Total from Standard Measures |  |  | Total from Standard Measures | 5435840.8 | 4415.2 | Specialized Measure |  | 1550.677
[5 empty] | Total from Specialized Measures |  |  | Total from Specialized Measures | 1841976.5 | 0 | Weighted EUL (yr) | 11.6929 | 269.6261
[9 empty] | 74.69% | Standard
[9 empty] | 25.31% | Specialized
1 Based on reported inventory of 3000 fixtures at NASSCO
2 Audits of ship repair facilities identify ~15% of ship repair consumption linked to US Navy living barges (15M kWh annually)