## Forecasting
[5 empty] | Number of risk events | [5 empty] | Actual |  | Projected risk events
| Table 7.1: Key recent and projected drivers of risk events | [11 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| Risk Event category | Cause category | # | Sub-cause category | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 5-yr avg 2017-2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | Unit(s) | Mitigations that affect driver rows for forecasting
x | Wire down event - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | 10 | 22 | 31 | 13 | 12 | 13 | 12 | 16.2 | 3.8697 | 3.8697 | 3.8697 | 3.8697 | 3.6895 | 3.6895 | 3.6895 | 3.6895 | # risk events (excluding ignitions) | UG, CC, OH Hard, Enh Veg Mgmt
| Wire down event - Distribution |  | 1.b. | Animal contact- Distribution | 0 | 8 | 2 | 2 | 0 | 3 | 4 | 2.2 | 0.54438 | 0.54438 | 0.54438 | 0.54438 | 0.53875 | 0.53875 | 0.53875 | 0.53875 | # risk events (excluding ignitions) | UG, CC, OH Hard
| Wire down event - Distribution |  | 1.c. | Balloon contact- Distribution | 1 | 5 | 8 | 3 | 5 | 5 | 3 | 4.8 | 1.1951 | 1.1951 | 1.1951 | 1.1951 | 1.1903 | 1.1903 | 1.1903 | 1.1903 | # risk events (excluding ignitions) | UG, CC
| Wire down event - Distribution |  | 1.d. | Vehicle contact- Distribution | 6 | 13 | 17 | 23 | 28 | 33 | 22 | 24.6 | 6.1323 | 6.1323 | 6.1323 | 6.1323 | 6.1146 | 6.1146 | 6.1146 | 6.1146 | # risk events (excluding ignitions) | UG
| Wire down event - Distribution |  | 1.e. | Other contact from object - Distribution | 8 | 15 | 18 | 6 | 13 | 3 | 2 | 8.4 | 2.091 | 2.091 | 2.091 | 2.091 | 2.0819 | 2.0819 | 2.0819 | 2.0819 | # risk events (excluding ignitions) | UG
| Wire down event - Distribution | 2. Equipment / facility failure - Distribution | 2.a. | Connector damage or failure- Distribution | 7 | 2 | 0 | 7 | 6 | 11 | 15 | 7.8 | 1.9203 | 1.9203 | 1.9203 | 1.9203 | 1.8906 | 1.8906 | 1.8906 | 1.8906 | # risk events (excluding ignitions) | UG, CC, OH Hard, Hotline Clamps, Dist IR
| Wire down event - Distribution |  | 2.b. | Splice damage or failure — Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | UG, Dist IR
| Wire down event - Distribution |  | 2.c. | Crossarm damage or failure - Distribution | 0 | 0 | 0 | 1 | 3 | 1 | 1 | 1.2 | 0.29785 | 0.29785 | 0.29785 | 0.29785 | 0.2957 | 0.2957 | 0.2957 | 0.2957 | # risk events (excluding ignitions) | UG, CC, OH Hard, Drone
| Wire down event - Distribution |  | 2.d. | Insulator damage or failure- Distribution | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.2 | 0.049543 | 0.049543 | 0.049543 | 0.049543 | 0.049085 | 0.049085 | 0.049085 | 0.049085 | # risk events (excluding ignitions) | UG, CC, OH Hard, Drone
| Wire down event - Distribution |  | 2.e. | Lightning arrestor damage or failure- Distribution | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0.2 | 0.049494 | 0.049494 | 0.049494 | 0.049494 | 0.048989 | 0.048989 | 0.048989 | 0.048989 | # risk events (excluding ignitions) | UG
| Wire down event - Distribution |  | 2.f. | Tap damage or failure - Distribution | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | UG, CC, OH Hard, Drone, Dist IR
| Wire down event - Distribution |  | 2.g. | Tie wire damage or failure - Distribution | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | UG, CC, OH Hard, Drone
| Wire down event - Distribution |  | 2.h. | Other - Distribution | 27 | 71 | 60 | 35 | 40 | 18 | 33 | 37.2 | 9.2277 | 9.2277 | 9.2277 | 9.2277 | 9.1554 | 9.1554 | 9.1554 | 9.1554 | # risk events (excluding ignitions) | UG, CC, OH Hard, Drone
| Wire down event - Distribution | 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.2 | 0.049219 | 0.049219 | 0.049219 | 0.049219 | 0.048438 | 0.048438 | 0.048438 | 0.048438 | # risk events (excluding ignitions) | UG, CC, OH Hard
| Wire down event - Distribution | 4. Contamination - Distribution | 4.a. | Contamination - Distribution | 0 | 0 | 0 | 2 | 2 | 4 | 0 | 1.6 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39829 | 0.39829 | 0.39829 | 0.39829 | # risk events (excluding ignitions) | UG, CC,
| Wire down event - Distribution | 5. Utility work / Operation | 5.a. | Utility work / Operation | 1 | 1 | 1 | 2 | 1 | 0 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | # risk events (excluding ignitions) | no mitigation
| Wire down event - Distribution | 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | 0 | 0 | 0 | 1 | 1 | 2 | 4 | 1.6 | 0.39982 | 0.39982 | 0.39982 | 0.39982 | 0.39964 | 0.39964 | 0.39964 | 0.39964 | # risk events (excluding ignitions) | UG
| Wire down event - Distribution | 7. Other- Distribution | 7.a. | All Other- Distribution | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | UG
| Wire down event - Distribution | 8. Unknown- Distribution | 8.a. | Unknown - Distribution | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | UG, CC, OH Hard
x | Wire down event - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission |  | 9.b. | Animal contact- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission |  | 9.c. | Balloon contact- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission |  | 9.d. | Vehicle contact- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event - Transmission |  | 9.e. | Other contact from object - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission | 10. Equipment / facility failure - Transmission | 10.a. | Connector damage or failure- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission |  | 10.b. | Splice damage or failure — Transmission | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission |  | 10.c. | Crossarm damage or failure - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission |  | 10.d. | Insulator damage or failure- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission |  | 10.e. | Lightning arrestor damage or failure- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event - Transmission |  | 10.f. | Tap damage or failure - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission |  | 10.g. | Tie wire damage or failure - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission |  | 10.h. | Other - Transmission | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.4 | 0.0995 | 0.0995 | 0.0995 | 0.0995 | 0.099 | 0.099 | 0.099 | 0.099 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission | 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission | 12. Contamination - Transmission | 12.a. | Contamination - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission | 13. Utility work / Operation | 13.a. | Utility work / Operation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event - Transmission | 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event - Transmission | 15. Other- Transmission | 15.a. | All Other- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Wire down event - Transmission | 16. Unknown- Transmission | 16.a. | Unknown - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
x | Outage - Distribution | 17. Contact from object - Distribution | 17.a. | Veg. contact- Distribution | 27 | 61 | 70 | 34 | 27 | 31 | 41 | 40.6 | 9.6982 | 9.6982 | 9.6982 | 9.6982 | 9.2465 | 9.2465 | 9.2465 | 9.2465 | # risk events (excluding ignitions) | UG, CC, OH Hard, Enh Veg Mgmt
| Outage - Distribution |  | 17.b. | Animal contact- Distribution | 70 | 80 | 77 | 74 | 89 | 95 | 86 | 84.2 | 20.8347 | 20.8347 | 20.8347 | 20.8347 | 20.6195 | 20.6195 | 20.6195 | 20.6195 | # risk events (excluding ignitions) | UG, CC, OH Hard
| Outage - Distribution |  | 17.c. | Balloon contact- Distribution | 70 | 84 | 120 | 112 | 93 | 111 | 136 | 114.4 | 28.4843 | 28.4843 | 28.4843 | 28.4843 | 28.3685 | 28.3685 | 28.3685 | 28.3685 | # risk events (excluding ignitions) | UG, CC
| Outage - Distribution |  | 17.d. | Vehicle contact- Distribution | 94 | 96 | 93 | 99 | 100 | 107 | 120 | 103.8 | 25.8752 | 25.8752 | 25.8752 | 25.8752 | 25.8005 | 25.8005 | 25.8005 | 25.8005 | # risk events (excluding ignitions) | UG
| Outage - Distribution |  | 17.e. | Other contact from object - Distribution | 34 | 58 | 40 | 39 | 59 | 21 | 22 | 36.2 | 9.011 | 9.011 | 9.011 | 9.011 | 8.972 | 8.972 | 8.972 | 8.972 | # risk events (excluding ignitions) | UG, CC
| Outage - Distribution | 18. Equipment / facility failure - Distribution | 18.a. | Capacitor bank damage or failure- Distribution | 13 | 5 | 3 | 11 | 12 | 11 | 15 | 10.4 | 2.5762 | 2.5762 | 2.5762 | 2.5762 | 2.5525 | 2.5525 | 2.5525 | 2.5525 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.b. | Conductor damage or failure — Distribution | 35 | 87 | 71 | 49 | 56 | 32 | 61 | 53.8 | 13.3345 | 13.3345 | 13.3345 | 13.3345 | 13.219 | 13.219 | 13.219 | 13.219 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.c. | Fuse damage or failure - Distribution | 67 | 109 | 57 | 55 | 66 | 82 | 62 | 64.4 | 15.904 | 15.904 | 15.904 | 15.904 | 15.708 | 15.708 | 15.708 | 15.708 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.d. | Lightning arrestor damage or failure- Distribution | 22 | 28 | 26 | 20 | 28 | 23 | 38 | 27 | 6.6818 | 6.6818 | 6.6818 | 6.6818 | 6.6135 | 6.6135 | 6.6135 | 6.6135 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.e. | Switch damage or failure- Distribution | 8 | 15 | 10 | 19 | 15 | 17 | 12 | 14.6 | 3.613 | 3.613 | 3.613 | 3.613 | 3.576 | 3.576 | 3.576 | 3.576 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.f. | Pole damage or failure - Distribution | 20 | 32 | 62 | 23 | 67 | 31 | 46 | 45.8 | 11.3487 | 11.3487 | 11.3487 | 11.3487 | 11.2475 | 11.2475 | 11.2475 | 11.2475 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.g. | Insulator and brushing damage or failure - Distribution | 2 | 7 | 7 | 9 | 10 | 4 | 11 | 8.2 | 2.0312 | 2.0312 | 2.0312 | 2.0312 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.h. | Crossarm damage or failure - Distribution | 4 | 14 | 20 | 30 | 33 | 29 | 43 | 31 | 7.6945 | 7.6945 | 7.6945 | 7.6945 | 7.639 | 7.639 | 7.639 | 7.639 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.i. | Voltage regulator / booster damage or failure - Distribution | 0 | 0 | 1 | 1 | 0 | 1 | 3 | 1.2 | 0.299 | 0.299 | 0.299 | 0.299 | 0.298 | 0.298 | 0.298 | 0.298 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.j. | Recloser damage or failure - Distribution | 4 | 0 | 0 | 1 | 2 | 5 | 1 | 1.8 | 0.448 | 0.448 | 0.448 | 0.448 | 0.446 | 0.446 | 0.446 | 0.446 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.k. | Anchor / guy damage or failure - Distribution | 2 | 3 | 1 | 2 | 1 | 1 | 2 | 1.4 | 0.345 | 0.345 | 0.345 | 0.345 | 0.34 | 0.34 | 0.34 | 0.34 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.l. | Sectionalizer damage or failure - Distribution | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.m. | Connection device damage or failure - Distribution | 54 | 57 | 40 | 50 | 64 | 65 | 71 | 58 | 14.2792 | 14.2792 | 14.2792 | 14.2792 | 14.0585 | 14.0585 | 14.0585 | 14.0585 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone, Hotline Clamps, Dist IR
| Outage - Distribution |  | 18.n. | Transformer damage or failure - Distribution | 72 | 52 | 38 | 63 | 46 | 55 | 73 | 55 | 13.602 | 13.602 | 13.602 | 13.602 | 13.454 | 13.454 | 13.454 | 13.454 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution |  | 18.o. | Other - Distribution | 2 | 12 | 13 | 19 | 25 | 4 | 74 | 27 | 6.712 | 6.712 | 6.712 | 6.712 | 6.674 | 6.674 | 6.674 | 6.674 | # risk events (excluding ignitions) | UG, OH Hard, CC, Drone,
| Outage - Distribution | 19. Wire-to-wire contact - Distribution | 19.a. | Wire-to-wire contact / contamination- Distribution | 3 | 6 | 8 | 2 | 4 | 2 | 0 | 3.2 | 0.7875 | 0.7875 | 0.7875 | 0.7875 | 0.775 | 0.775 | 0.775 | 0.775 | # risk events (excluding ignitions) | UG, OH Hard, CC,
| Outage - Distribution | 20. Contamination - Distribution | 20.a. | Contamination - Distribution | 1 | 0 | 0 | 0 | 2 | 0 | 5 | 1.4 | 0.34925 | 0.34925 | 0.34925 | 0.34925 | 0.3485 | 0.3485 | 0.3485 | 0.3485 | # risk events (excluding ignitions) | UG, CC
| Outage - Distribution | 21. Utility work / Operation | 21.a. | Utility work / Operation | 6 | 9 | 5 | 9 | 9 | 30 | 16 | 13.8 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | # risk events (excluding ignitions) | no mitigation
| Outage - Distribution | 22. Vandalism / Theft - Distribution | 22.a. | Vandalism / Theft - Distribution | 2 | 4 | 1 | 3 | 2 | 6 | 10 | 4.4 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 1.099 | 1.099 | 1.099 | 1.099 | # risk events (excluding ignitions) | UG
| Outage - Distribution | 23. Other- Distribution | 23.a. | All Other- Distribution | 1 | 0 | 0 | 1 | 0 | 2 | 0 | 0.6 | 0.1495 | 0.1495 | 0.1495 | 0.1495 | 0.149 | 0.149 | 0.149 | 0.149 | # risk events (excluding ignitions) | UG
| Outage - Distribution | 24. Unknown- Distribution | 24.a. | Unknown - Distribution | 325 | 361 | 310 | 249 | 264 | 266 | 258 | 269.4 | 66.4153 | 66.4153 | 66.4153 | 66.4153 | 65.4805 | 65.4805 | 65.4805 | 65.4805 | # risk events (excluding ignitions) | UG, OH Hard, CC,
x | Outage - Transmission | 25. Contact from object - Transmission | 25.a. | Veg. contact- Transmission | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.04925 | 0.04925 | 0.04925 | 0.04925 | 0.0485 | 0.0485 | 0.0485 | 0.0485 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission |  | 25.b. | Animal contact- Transmission | 9 | 5 | 4 | 2 | 5 | 5 | 3 | 3.8 | 0.943 | 0.943 | 0.943 | 0.943 | 0.936 | 0.936 | 0.936 | 0.936 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission |  | 25.c. | Balloon contact- Transmission | 17 | 24 | 22 | 25 | 16 | 23 | 21 | 21.4 | 5.32 | 5.32 | 5.32 | 5.32 | 5.29 | 5.29 | 5.29 | 5.29 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission |  | 25.d. | Vehicle contact- Transmission | 1 | 2 | 0 | 3 | 1 | 1 | 5 | 2 | 0.5 | 0.5 | 0.5 | 0.5 | 0.125 | 0.125 | 0.125 | 0.125 | # risk events (excluding ignitions) | no mitigation
| Outage - Transmission |  | 25.e. | Other contact from object - Transmission | 1 | 0 | 2 | 1 | 3 | 0 | 0 | 1.2 | 0.298 | 0.298 | 0.298 | 0.298 | 0.296 | 0.296 | 0.296 | 0.296 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission | 26. Equipment / facility failure - Transmission | 26.a. | Capacitor bank damage or failure- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Outage - Transmission |  | 26.b. | Conductor damage or failure — Transmission | 2 | 6 | 6 | 2 | 0 | 6 | 1 | 3 | 0.7455 | 0.7455 | 0.7455 | 0.7455 | 0.741 | 0.741 | 0.741 | 0.741 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission |  | 26.c. | Fuse damage or failure - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Outage - Transmission |  | 26.d. | Lightning arrestor damage or failure- Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Outage - Transmission |  | 26.e. | Switch damage or failure- Transmission | 3 | 0 | 1 | 0 | 0 | 2 | 1 | 0.8 | 0.19875 | 0.19875 | 0.19875 | 0.19875 | 0.1975 | 0.1975 | 0.1975 | 0.1975 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission |  | 26.f. | Pole damage or failure - Transmission | 1 | 0 | 0 | 4 | 3 | 0 | 0 | 1.4 | 0.34775 | 0.34775 | 0.34775 | 0.34775 | 0.3455 | 0.3455 | 0.3455 | 0.3455 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission |  | 26.g. | Insulator and brushing damage or failure - Transmission | 29 | 13 | 6 | 3 | 8 | 0 | 22 | 7.8 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | # risk events (excluding ignitions) | no mitigation
| Outage - Transmission |  | 26.h. | Crossarm damage or failure - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission |  | 26.i. | Voltage regulator / booster damage or failure - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Outage - Transmission |  | 26.j. | Recloser damage or failure - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Outage - Transmission |  | 26.k. | Anchor / guy damage or failure - Transmission | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 0.04975 | 0.04975 | 0.04975 | 0.04975 | 0.0495 | 0.0495 | 0.0495 | 0.0495 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission |  | 26.l. | Sectionalizer damage or failure - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Outage - Transmission |  | 26.m. | Connection device damage or failure - Transmission | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.4 | 0.0995 | 0.0995 | 0.0995 | 0.0995 | 0.099 | 0.099 | 0.099 | 0.099 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission |  | 26.n. | Transformer damage or failure - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Outage - Transmission |  | 26.o. | Other - Transmission | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | # risk events (excluding ignitions) | no mitigation
| Outage - Transmission | 27. Wire-to-wire contact - Transmission | 27.a. | Wire-to-wire contact / contamination- Transmission | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission | 28. Contamination - Transmission | 28.a. | Contamination - Transmission | 3 | 8 | 0 | 3 | 1 | 1 | 1 | 1.2 | 0.29575 | 0.29575 | 0.29575 | 0.29575 | 0.2915 | 0.2915 | 0.2915 | 0.2915 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission | 29. Utility work / Operation | 29.a. | Utility work / Operation | 0 | 0 | 2 | 0 | 0 | 2 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.0625 | 0.0625 | 0.0625 | 0.0625 | # risk events (excluding ignitions) | no mitigation
| Outage - Transmission | 30. Vandalism / Theft - Transmission | 30.a. | Vandalism / Theft - Transmission | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Outage - Transmission | 31. Other- Transmission | 31.a. | All Other- Transmission | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | # risk events (excluding ignitions) | OH Trans
| Outage - Transmission | 32. Unknown- Transmission | 32.a. | Unknown - Transmission | 10 | 10 | 8 | 10 | 4 | 6 | 6 | 6.8 | 1.686 | 1.686 | 1.686 | 1.686 | 1.672 | 1.672 | 1.672 | 1.672 | # risk events (excluding ignitions) | OH Trans